## Slide 1: Solar-Thermal Heating Group
High Performance Building Investigation
Upland Hills Ecological Awareness Center
Oxford, Michigan
Ryan Grabow, Cheryl Smith, Jessica Turner, & Brent Wozniak
Professor Janice Means, P.E.
Lawrence Technological University

## Slide 2: Overview
Air Collector
Ductwork
Rock Storage
Building needs
Photos by Craig Necci

## Slide 3: Air Collector – Solar Thermal Air Based Collector Panels
Photo by Craig Necci

## Slide 4: Solar Exposure
Trees obstruct the sun from reaching the panels in the winter when heat is needed.
In December, a point on the panels will receive less than two hours of direct sunlight.
West
(Evening)
East
(Morning)
Winter
Summer

## Slide 5: Collector Tilt
58 degree slope aims the panels to maximize exposure to the winter sun.
Rule of thumb
Latitude + 15 ° to 20°

## Slide 6: Termosiphoning How it should work
10 square feet of solar collecting panels for every 100 square feet of floor space.
UHEAC is about 1800 square feet = 180 square feet of collecting panels or about 7 panels
Currently has 15 panels totaling 430 square feet of solar collecting area
www.motherearthnews.com/renewable-energy

## Slide 7: Is it working?

## Slide 8: Panel Construction

## Slide 9: Collector to Rock Storage

## Slide 10: Current problems
Aging system
Weeds between glass panes
Air flows from sides instead
of bottom
Duct work not properly sealed
Photo by Craig Necci

## Slide 11
Properly install collecting panels so that cold air flows in from bottom
  Reduce # of panels needed from 15 to 7
    If rock storage is not made effective
  Increase efficiency and effectiveness
Reseal all panels and incoming duct work
Replace any damaged panels and recoat real panels
What can be changed

## Slide 12: Ductwork

## Slide 13: Duct to Rock Storage Connection
(Drawing from Howell)

## Slide 14: Disconnected Controls
Disconnected furnace results in large openings within the duct system.
Control equipment is disconnected from dampers and thermostats.

## Slide 15: Disconnected Components
Control equipment is disconnected from dampers and thermostats.
Blower fan disconnected from the system.
Unintended openings in the rock storage

## Slide 16: Rock Storage
What is it
How should it work
Does it work
What can be changed

## Slide 17: Rock Storage Drawings & Pictures
West Elevation
Plan View
1
2
3
1
2
3

## Slide 18: Rock Storage Drawings & Pictures
South Elevation
East Elevation
1
2
3
3
4
4
2
1

## Slide 19: Installed Sensors
Pyranometer
Air Velocity Sensor
Temperature behind collector panels
Temperature within rock storage
5. Temperature within occupied space
1
4
3
5
2

## Slide 20: Sensor Locations
1
4
3
5
2
1.) Pyranometer
The Solar Radiation
light sensor measures
average light intensity
2.) Air Velocity Sensor
3.) Temperature Sensor
4. & 5.)
Temperature Sensors

## Slide 21: Collected Data December 12th, 2009
Chart: 
Temp, F (Exterior for Oxford, MI) | 17.6 | 17.6 | 18 | 19.4 | 19.4 | 17.6 | 18

## Slide 22: Collected Data December 12th, 2009
Chart: 
Temp, F (Exterior for Oxford, MI) | 17.6 | 17.6 | 18 | 19.4 | 19.4 | 17.6 | 18
Sunlight affecting temperature from collector; however, it is insufficient.

## Slide 23: Air Velocity Data
Chart: Air Velocity (fpm)
Erratic data largely falls outside the calibrated range. Increase opening size and check logger for averaging capability.

## Slide 24: Recommendations
Restore duct system to an operable state.
  Close unintended openings.
  Reinstall blower fan.
  Revaluate system via manual operation of dampers.
  Replace supplemental heat system.
  Salvage / replace automated control system.
Replace coniferous trees south of the building with short deciduous tress.
Revaluate prior to modifying air collector panels.

## Slide 25: UHEAC Energy Audit
September UHEAC Energy Usage
244 KW-hrs/month
HPBI Energy Audit
8.34 KW-hrs/day
8.34 x 31 (days) = 259 KW-hours/month
[(244-259) / 244] x 100 = 6% difference
Note: Highest Usage
*Highest power usage is
the desktop computer
8.34 KW-hrs/day

## Slide 26: UHEAC : Floor Plans Device : Energy Ratios : per room basis
2 :414
7 : 725
# Devices : Energy Usage (Watt-hrs/day)
Rounded up
3 : 14
2 : 28
8 : 90
10 : 4,658
5 : 1968
1 : 7
1 : 7
2 : 50

## Slide 27: UHEAC : Floor Plans Device : Energy Ratios : per room basis
2 : 12
# Devices : Energy Usage (Watt-hrs/day)
Rounded up

## Slide 28: Energy Audit Breakdown
Office
Meeting Room

## Slide 29: Energy Audit Breakdown
Battery Closet
Kitchen

## Slide 30: Software Evaluation
Software | Website | Comments | Cost
ESP-r | apps1.eere.energy.gov/buildings/tools_directory/software.cfm/ID=39/pagename_submenu=load_calculation/pagename_menu=whole_building_analysis/pagename=subjects | Whole building analysis. An EnergyPlus Interface. Compatible with AutoCAD and Ecotect. | Free
ECOTECT | www.squ1.com/ | Whole building analysis. An EnergyPlus Interface. Extensive program. Learning curve involved. Compatible with AutoCAD. | Student License $75
Energy Plus | apps1.eere.energy.gov/buildings/energyplus/ | Whole building analysis. Most comprehensive, state of the art, energy software available from the Dept of Energy. | Free
EP-Launch, IDF Editor, & Open Studio | apps1.eere.energy.gov/buildings/energyplus/ep_utilities.cfm#idfeditor | An EnergyPlus Utility. Helps create input files and run simulations. | Free-Part of Energy Plus
Energy Plugged & EP-Quick | apps1.eere.energy.gov/buildings/energyplus/ep_utilities.cfm#idfeditor | Data interface for EnergyPlus. This is a plugin for AutoDesk AutoCAD to allow for easy input of data to EnergyPlus. | Free

## Slide 31: Supplementary Resources
Electrical Energy Usage Survey and Analysis
Energy Modeling Software Evaluation
Weather Data Sources Documentation
Sunlight and Sneezing Literature Search
Assistance to Greenroof Group:
Provided assistance on how to measure greenroof performance
Conducted search for greenroof modeling software
Solar Radiation Data